## Sheet1
Name | description | price_starttime | demand_starttime | length | gas_turbine_minload_electricity_capacity | gas_turbine_maxload_electricity_capacity | gas_turbine_minload_electricity_efficiency | gas_turbine_maxload_electricity_efficiency | gas_turbine_minload_heat_efficiency | gas_turbine_maxload_heat_efficiency | gas_boiler_efficiency | gas_boiler_capacity | e_boiler_efficiency | e_boiler_capacity | hrsg_efficiency | hrsg_capacity | elec_offtake_contract_param_a | elec_offtake_contract_param_b | elec_injection_contract_param_a | elec_injection_contract_param_b | elec_grid_cost_energy | elec_grid_cost_power_peak | elec_grid_cost_power_fixed | elec_grid_cost_max_tariff | elec_offtake_tax_energy | gas_offtake_contract_param_a | gas_offtake_contract_param_b | gas_grid_cost_energy
Flex_0 | CHP (GT) is always running at nominal capacity, post firing is used for additional steam production. Gas boiler is not economically dispatched. No eboiler. | 2024-01-01 | 2022-01-01 | 8760 | 5.895 | 0.655 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_1.1 | Identical to Flex_0, but with modulation of the GT by 10%. | 2024-01-01 | 2022-01-01 | 8760 | 5.895 | 0.655 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_1.2 | Identical to Flex_0, but with modulation of the GT by 20%. | 2024-01-01 | 2022-01-01 | 8760 | 5.24 | 1.31 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_1.3 | Identical to Flex_0, but with modulation of the GT by 30%. | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_1.4 | Identical to Flex_0, but with modulation of the GT by 40%. | 2024-01-01 | 2022-01-01 | 8760 | 3.93 | 2.62 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_1.5 | Identical to Flex_0, but with modulation of the GT by 50%. | 2024-01-01 | 2022-01-01 | 8760 | 3.275 | 3.275 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_2.3 | Identical to Flex_2.3, but with economical dispatch of the gas boiler (shutdown of chp possible - stack undoubled) | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_3.1 | Identical to Flex_2.3, but with large eboiler on Elia, with full grid tariffs | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 25 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 7.54 | 1.8472 | 1.1338 | 0 | 10.91 | 1 | 0.55 | 5
Flex_3.11 | Identical to Flex_2.3, but with large eboiler on Elia, with 80% grid tariff reduction | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 25 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 1.508 | 0.36944 | 0.22677 | 0 | 10.91 | 1 | 0.55 | 5
Flex_3.2 | Identical to Flex_2.3, but with medium eboiler on Fluvius Post, with full grid tariffs | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 15 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 0.3603 | 4.02 | 3.3509 | 0 | 10.91 | 1 | 0.55 | 5
Flex_3.3 | Identical to Flex_2.3, but with small eboiler on Fluvius Ring, with full grid tariffs | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 8 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_4 | Full gas boiler (no CHP, no eboiler) | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 0 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Flex_5.1 | Identical to Flex_4, but with large eboiler on Elia, with full grid tariffs | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 25 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 7.54 | 1.8472 | 1.1338 | 0 | 10.91 | 1 | 0.55 | 5
Flex_5.11 | Identical to Flex_4, but with large eboiler on Elia, with 80% grid tariff reduction | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 25 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 1.508 | 0.36944 | 0.22677 | 0 | 10.91 | 1 | 0.55 | 5
Flex_5.2 | Identical to Flex_4, but with medium eboiler on Fluvius Post, with full grid tariffs | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 15 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 0.3603 | 4.02 | 3.3509 | 0 | 10.91 | 1 | 0.55 | 5
Flex_5.3 | Identical to Flex_4, but with small eboiler on Fluvius Ring, with full grid tariffs | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 8 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 4.88 | 3.5127 | 0 | 10.91 | 1 | 0.55 | 5
Note on W1: Jens Baetens: only the part which is influenced by the peak; so not the "toegangsvermogen" for Fluvius or the "tarieven voor het beschikbaar gestelde vermogen" for Elia
Note on X1: this is the part which is fixed, so always to be paid, no matter the dispatch logic
Note on F13: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G13: Jens Baetens: workaround; cannot be 0
Note on F14: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G14: Jens Baetens: workaround; cannot be 0
Note on F15: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G15: Jens Baetens: workaround; cannot be 0
Note on F16: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G16: Jens Baetens: workaround; cannot be 0
Note on F17: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G17: Jens Baetens: workaround; cannot be 0

## not_simulated
Name | description | price_starttime | demand_starttime | length | gas_turbine_minload_electricity_capacity | gas_turbine_maxload_electricity_capacity | gas_turbine_minload_electricity_efficiency | gas_turbine_maxload_electricity_efficiency | gas_turbine_minload_heat_efficiency | gas_turbine_maxload_heat_efficiency | gas_boiler_efficiency | gas_boiler_capacity | e_boiler_efficiency | e_boiler_capacity | hrsg_efficiency | hrsg_capacity | elec_offtake_contract_param_a | elec_offtake_contract_param_b | elec_injection_contract_param_a | elec_injection_contract_param_b | elec_grid_cost_energy | elec_grid_cost_power_peak | elec_grid_cost_power_fixed | elec_grid_cost_max_tariff | elec_offtake_tax_energy | gas_offtake_contract_param_a | gas_offtake_contract_param_b | gas_grid_cost_energy
Flex_0_max_tariff | CHP (GT) is always running at nominal capacity, post firing is used for additional steam production. Gas boiler is not economically dispatched. No eboiler. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 5.895 | 0.655 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_1.1_max_tariff | Identical to Flex_0, but with modulation of the GT by 10%. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 5.895 | 0.655 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_1.2_max_tariff | Identical to Flex_0, but with modulation of the GT by 20%. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 5.24 | 1.31 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_1.3_max_tariff | Identical to Flex_0, but with modulation of the GT by 30%. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_1.4_max_tariff | Identical to Flex_0, but with modulation of the GT by 40%. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 3.93 | 2.62 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_1.5_max_tariff | Identical to Flex_0, but with modulation of the GT by 50%. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 3.275 | 3.275 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_2.3_max_tariff | Identical to Flex_2.3, but with economical dispatch of the gas boiler (shutdown of chp possible - stack undoubled). Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 0 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_3.1_max_tariff | Identical to Flex_2.3, but with large eboiler on Elia, with full grid tariffs. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 25 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 7.54 | 0 | 1.1338 | 0 | 10.91 | 1 | 0.55 | 5
Flex_3.11_max_tariff | Identical to Flex_2.3, but with large eboiler on Elia, with 80% grid tariff reduction. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 25 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 1.508 | 0 | 0.22677 | 0 | 10.91 | 1 | 0.55 | 5
Flex_3.2_max_tariff | Identical to Flex_2.3, but with medium eboiler on Fluvius Post, with full grid tariffs. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 15 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 0.3603 | 0 | 3.3509 | 59 | 10.91 | 1 | 0.55 | 5
Flex_3.3_max_tariff | Identical to Flex_2.3, but with small eboiler on Fluvius Ring, with full grid tariffs. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 4.585 | 1.965 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 24 | 0.99 | 8 | 1 | 12 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_4_max_tariff | Full gas boiler (no CHP, no eboiler). Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 0 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Flex_5.1_max_tariff | Identical to Flex_4, but with large eboiler on Elia, with full grid tariffs. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 25 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 7.54 | 0 | 1.1338 | 0 | 10.91 | 1 | 0.55 | 5
Flex_5.11_max_tariff | Identical to Flex_4, but with large eboiler on Elia, with 80% grid tariff reduction. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 25 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 1.508 | 0 | 0.22677 | 0 | 10.91 | 1 | 0.55 | 5
Flex_5.2_max_tariff | Identical to Flex_4, but with medium eboiler on Fluvius Post, with full grid tariffs. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 15 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 0.3603 | 0 | 3.3509 | 59 | 10.91 | 1 | 0.55 | 5
Flex_5.3_max_tariff | Identical to Flex_4, but with small eboiler on Fluvius Ring, with full grid tariffs. Max tariff (no peak tariff) | 2024-01-01 | 2022-01-01 | 8760 | 200 | 1 | 0.31 | 0.31 | 0.46 | 0.46 | 0.85 | 40 | 0.99 | 8 | 1 | 0 | 1.029 | 13.7 | 1 | 6.49 | 5.0042 | 0 | 3.5127 | 150 | 10.91 | 1 | 0.55 | 5
Note on W1: Jens Baetens: only the part which is influenced by the peak; so not the "toegangsvermogen" for Fluvius or the "tarieven voor het beschikbaar gestelde vermogen" for Elia
Note on X1: this is the part which is fixed, so always to be paid, no matter the dispatch logic
Note on F13: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G13: Jens Baetens: workaround; cannot be 0
Note on F14: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G14: Jens Baetens: workaround; cannot be 0
Note on F15: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G15: Jens Baetens: workaround; cannot be 0
Note on F16: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G16: Jens Baetens: workaround; cannot be 0
Note on F17: Jens Baetens: workaround so to make sure the CHP is not dispatched
Note on G17: Jens Baetens: workaround; cannot be 0